## Sheet1
Incident ID | Date | Location | Incident Type | Measured Value | Regulatory Requirement | Resolution Method | Incident Type | Count
1 | 2024-05-27 | SB01H090P, 195 Constellation Dr. | Low Chlorine | Total: 0.12 mg/L, Free: 0.02 mg/L, Combined: 0.1 mg/L | Min Combined Chlorine of 0.25 mg/L or Free Chlorine of 0.05 mg/L | Watermain flushed to restore chlorine | Low Chlorine | 2
2 | 2024-06-19 | D-SS-09, 51 Robinhood Dr. | Total Coliforms | Present | Not Detectable | Resampled adverse location, upstream and downstream. All results passed. | Total Coliforms | 3
3 | 2024-06-25 | 7-15, Pumping Station HD007, 293 Highland Rd. W. | Total Coliforms | Present | Not Detectable | Resampled adverse location, upstream and downstream. All results passed.
4 | 2024-07-23 | H-SS-37, Opposite 54 Mars Ave. | Low Chlorine | Total: 0.13 mg/L, Free: 0.02 mg/L, Combined: 0.11 mg/L | Min Combined Chlorine of 0.25 mg/L or Free Chlorine of 0.05 mg/L | Watermain flushed to restore chlorine
5 | 2024-07-26 | H-SS-32, 363 Wellington St. N. | Total Coliforms | Present | Not Detectable | Resampled adverse location, upstream and downstream. All results passed.
Water Quality Incidents - Summary Report
Report generated from Swim Guide Data - Appendix 'A' to Report PW25006